## Annex II TS - Prilog II TS
ANNEX II: TECHNICAL SPECIFICATION WITHIN PROCUREMENT NOTICE 02/2021
PRILOG II: TEHNIČKA SPECIFIKACIJA UZ OBAVIJEST O NABAVI 02/2021
Procurement subject: Devulcanizate production line cooling system
Predmet nabave: Sustav hlađenja linije za proizvodnju devulkanizata
Summary: Subject of procurement is supply, delivery, installation, unloading, commissioning and warranty for quality of sold goods for Devulcanizate production line cooling system. The Devulcanizate production line cooling system is used to cool the devulcanizate production line. It is an integral part of the Devulcanizate production line, which is necessary for industrial research and development of new products. Without a cooling system the devulcanizate production line cannot function. The Devulcanizate production line cooling system includes: a) Water cooler b) Hydromodule c) Piping and fittings b) Thermal insulation of pipelines e) Protective lining of the pipeline ** specifications will be given later in OVERVIEW.
Sažetak: Predmet nabave je kupnja, isporuka, instalacija, puštanje u pogon i usluga jamstva za ispravnost prodane robe za Sustav hlađenja linije za proizvodnju devulkanizata. Sustav hlađenja linije za proizvodnju devulkanizata služi za hlađenje linije za proizvodnju devulkanizata. Sastavni je dio Linije za proizvodnju devulkanizata, a koja je neophodna za industrijsko istraživanje i razvoj novih proizvoda. Bez Sustava za hlađenje linija za proizvodnju devulkanizata ne može funkcionirati. Sustav hlađenja linije za proizvodnju devulkanizata uključuje: a) Rashladnik vode b) Hidromodul c) Cjevovod i armaturu b) Toplinsku izolaciju cjevovoda e) Zaštitnu oblogu cjevovoda **specifikacije će biti naknadno dane u OVERVIEW.
Column 1-2 should be completed by the Contracting Authority. Column 3-4 should be completed by the Tenderer (Column 3 is to be filled in by the Tenderer and must detail what is offered, Column 4 allows the Tenderer to make comments on its proposed supply and to make eventual references to the documentation). Column 5 is reserved for the Evaluation Committee. Unless otherwise defined, the requirements defined in the Technical Specifications represent the minimum technical characteristics that the offered goods must meet. The Tenderer MUST FILL in the column 3. "Offered specifications" defining in detail the technical specifications of the offered goods (NOTE: the Tenderer fills in the technical specifications by entering the exact characteristics of the offered goods, avoiding filling in the column only with words such as "satisfies", "YES", “NO” or "corresponds to what is offered"). In order for the offer to be considered valid, Subject of procurement must satisfy everything required in the form of Technical Specifications. In case of doubt as to the veracity of the data stated in the offered technical specifications, the Contracting authority reserves the right to verify the data in any appropriate way (eg by checking the data published on the website of the manufacturer, distributor or may contact the manufacturer, etc.). Stupce 1-2 popunjava Naručitelj. Stupce 3-4 popunjava Ponuditelj (u stupcu 3 se navode tehnički podaci o ponuđenoj opremi, a u stupcu 4 Ponuditelj može navesti komentar). Stupac 5 popunjava Povjerenstvo za ocjenu ponuda. Ako nije drugačije definirano, zahtjevi definirani Tehničkim specifikacijama predstavljaju minimalne tehničke karakteristike koje ponuđena roba mora zadovoljavati. Ponuditelj OBAVEZNO POPUNJAVA stupac 3. «Ponuđene specifikacije» definirajući detaljno tehničke specifikacije ponuđene robe (NAPOMENA: ponuditelj popunjava tehničke specifikacije upisujući točne karakteristike ponuđene robe, izbjegavajući pri tome popunjavanje stupca samo riječima kao što su npr. „zadovoljava“, „DA“, „NE“ ili „odgovara traženom“). U slučaju postojanja sumnje u istinitost podataka navedenih u ponuđenim tehničkim specifikacijama, Naručitelj zadržava pravo provjere navedenih podataka bilo kojim prikladnim sredstvom / načinom (npr. provjerom podataka objavljenih na internet stranicama proizvođača, distributera ili se može obratiti proizvođaču i sl.)."
1 – GENERAL REQUIREMENTS / OPĆI ZAHTJEVI 1.1 General requirements applying to all of the items / Opći zahtjevi primjenjivi na sve stavke
1. All technical requirements listed in the technical specifications are to be considered „or equal“./ Za sve tražene specifikacije/karakteristike koje su navedene u tehničkim specifikacijama vrijedi "ili jednakovrijedno“.
2. All equipments should be new, unused, not refurbished, most recent models and should have no any defects. The tenderers should not propose any equipment that is announced as end-of-line by the manufacturer./ Oprema mora biti nova, nekorištena, neobnovljena, najnoviji model i mora biti bez defekata. Dobavljači ne smiju predložiti opremu za koju je najavljen kraj linije proizvoda od strane proizvođača.
3. All required components that are not stated explicitly in this Technical Specifications document but are necessary for successful solution to the specifications herein shall be proposed./ Sve potrebne komponente koje nisu eksplicitno navedene u ovoj tehničkoj specifikaciji, a neophodne su za funkcionalno riješenje prema specifikacijama moraju biti predložene.
4. All software shall be full version licensed to GUMIIMPEX - GUMI RECIKLAŽA I PROIZVODNJA d.o.o., with no licence expiration limitations/ Sav software mora biti puna verzija licencirana na GUMIIMPEX - GUMI RECIKLAŽA I PROIZVODNJA d.o.o., bez vremenskog ograničenja isteka licence.
1.2 Training requirements / Zahtjevi za edukaciju
1. The Contractor shall perform the on-site trainings of users in start-up, set-up, operation and use of all the equipment supplied. Instruction and training in the use of the equipment must be provided and conducted at the time of installation. / Dobavljač će izvršiti obuku osoblja na lokaciji za upućivanje, podešavanje i korištenje sve isporučene opreme. Upute i obuka za upotrebu moraju biti dostupne i provedene u vrijeme instalacije opreme.
1 | 2 |  | 3
| Specifications Required/ Zahtjevane specifikacije |  | Specifications Offered/ Ponuđene specifikacije
DUST EXTRACTION AND FILTRATION SYSTEM WITH MOUNTING / SUSTAV ZA OTPRAŠIVANJE I FILTRIRANJE S MONTAŽOM SET/ KOMPLET
1. | WATER COOLER / RASHLADNIK VODE/1 pc / 1 kom
| Technical specification / Tehničke karakteristike | Water cooler with air cooled condenser with microchannel technology in a plastic coated tin housing. Water cooler with two refrigeration circuits each with two scroll compressors. Each refrigeration circuit consists of a compressor, condenser, electronic expansion valve, ball valves, control glass, filter drier, filling valve, pressure switch and probe with all the necessary protective fittings and automation for safe operation. The device is equipped with a free cooling system. General data: - Capacity: Q0=230kW minimum - Media: ethylene glycol 35% (included media, filling and venting of the system) - System: 23/18 °C - Working substance: R32 - Dimensions: 3800x2400x2600mm maximum - Device weight: 2200kg maximum / Rashladnik vode sa zrakom hlađenim kondenzatorom sa microchannel tehnologijom u limenom plastificiranom kućištu. Rashladnik vode sa dva rashladna kruga svaki sa po dva scroll kompresora. Svaki rashladni krug sastoji se od kompresora, kondenzatora, elektronskog ekspanzionog ventila, kuglastih ventila, kontrolnog stakla, filter sušača, ventila za punjenje, presostata i sondi sa svom potrebnom zaštitnom armaturom i automatikoom za siguran rad. Uređaj je opremljen sa free cooling sustavom. Generalni podaci: - Capacity: Q0=230kW minimum - Media: etilen glikol 35% (uključen medij, punjenje i odzračivanje sustava) - Sistem: 23/18 °C - Radna tvar: R32 - Dimenzije: 3800x2400x2600mm maksimum - Masa uređaja: 2200kg maksimum
2. | HYDROMODULE / HIDROMODUL / 1pcs/1kom
| Technical specification / Tehničke karakteristike | Consists of an insulated tank with a volume of 1000 liters with associated fittings, working and backup pump, shut-off valves, expansion vessel, safety valve, non-return valves, filter, filling and emptying tap, etc. All in a protective tin housing for outdoor installation. / Sastoji se od izoliranog spremnika volumena 1000 litara sa pripadajućom armaturom, radnom i rezervnom pumpom, zapornim ventilima, ekspanzijskom posudom, sigurnosnim ventilom, nepovratnim ventilima, filterom, slavinom za punjenje i pražnjenje itd. Sve u zaštitnom limenom kućištu za vanjsku ugradnju.
3. | PIPING AND FITTINGS / CJEVOVOD I ARMATURA / 1set/1komplet
| Technical specification / Tehničke karakteristike | Associated piping and fittings for connecting water coolers, hydraulic modules and consumers. / Pripadaući cjevovod i armatura za spajanje rashladnika vode, hidromodula i potrošača.
Refrigerant piping from water cooler to consumer made of steel welded pipes dimensions: DN 100 114,3x3,2mm 40m DN 80 88,9x2,9mm 12m DN 65 76,1x3,6mm 16m DN 40 48,3x3,2mm 69m DN 20 26,9x2,6mm 26m / Cjevovod rashladnog medija od rashladnika vode do potrošača izrađen od čeličnih šavnih cijevi dimenzija: DN 100 114,3x3,2mm 40m DN 80 88,9x2,9mm 12m DN 65 76,1x3,6mm 16m DN 40 48,3x3,2mm 69m DN 20 26,9x2,6mm 26m
Steel pipe bends for welding, dimensions: DN 100 - 6 pieces DN 80 - 2 pieces DN 65 - 4 pieces DN 40 - 14 pieces DN 20 - 8 pieces / Čelični cijevni lukovi za zavarivanje, dimenzija: DN 100 - 6 komada DN 80 - 2 komada DN 65 - 4 komada DN 40 - 14 komada DN 20 - 8 komada
Steel T-pieces for welding, dimensions: DN 100 - 2 pieces DN 80 - 4 pieces DN 40 - 4 pieces / Čelični T-komadi za zavarivanje, dimenzija: DN 100 - 2 komada DN 80 - 4 komada DN 40 - 4 komada
Steel reduction piece for welding, dimensions: NO 100/NO 80 - 2 pieces NO 100/NO 40 - 2 pieces NO 80 / NO 40 - 4 pieces NO 80/NO 65 - 2 pieces NO 40/NO 20 - 4 pieces NO 40/NO 25 - 2 pieces / Čelični prijelazni komad za zavarivanje, dimenzija: NO 100/NO 80 - 2 komada NO 100/NO 40 - 2 komada NO 80 / NO 40 - 4 komada NO 80/NO 65 - 2 komada NO 40/NO 20 - 4 komada NO 40/NO 25 - 2 komada
Butterfly valve with handle for connection to water cooler and hydromodule, flange connection, dimensions: NO 100 - 4 pieces / Leptirasta zaklopka sa ručkom za spoj na rashladnik vode i hidromodul, prirubnički spoj, dimenzija: NO 100 - 4 komada
Steel weld neck flanges with screws and seal, dimensions: NO 100 - 8 pieces / Čelične grlate prirubnice sa vijcima i brtvom, dimenzija: NO 100 - 8 komada
Pipe compensator (pipe) for installation on water cooler and pipeline connections, dimensions: NO 100 - 2 pieces / Cijevni kompenzator (cijev) za ugradnju na priključke rashladnika vode i cjevovoda, dimenzija: NO 100 - 2 komada
Strainer with flange connection, dimensions: NO 100 - 2 komada / Hvatač nečistoća prirubnički spoj, dimenzija: NO 100 - 2 komada
Ball valves for connecting pipelines to consumer places, dimensions: DN 65 - 2 pieces DN 40 - 8 pieces DN 25 - 2 pieces DN 20 - 2 pieces / Kuglasti ventili za spajanje cjevovoda sa potrošačkim mjestima, dimenzija: DN 65 - 2 komada DN 40 - 8 komada DN 25 - 2 komada DN 20 - 2 komada
Flexible connections (vibration compensators) for connection of pipelines with consumer places, dimensions: DN 20 - 6 komada DN 25 - 2 komada DN 40 - 4 komada / Fleksibilni priključci (kompenzatori vibracija) za spoj cjevovoda sa potrošačkim mjestima, dimenzija: DN 20 - 6 komada DN 25 - 2 komada DN 40 - 4 komada
Faucet for filling and emptying at every consumer place - 6 pieces / Slavina za punjenje i pražnjenje kod svakog potrošačkog mjesta - 6 komada
Automatic vent valve for installation on supply and return line, together with pipe connection 1/2 '' - 2 sets / Automatski odzračni ventil za ugradnju na dolazni i povratni vod, zajedno sa cijevnim priključkom 1/2'' - 2 kompleta
Industrial thermometer with R1/2 "connection and connecting pipeline. Thermometer for measuring range from 0 to 130 ° C degrees - 2 pieces / Industrijski termometar sa priključkom R1/2" i spojnim cjevovodom. Termometar za mjerno područje od 0 do 130°C stupnjeva - 2 komada
Manometer with connection R1 / 2 ". Manometer for measuring range 0 to 6 bar - 2 sets / Manometar sa priključkom R1/2". Manometar za mjerno podrucje 0 do 6 bara. - 2 kompleta
4. | THERMAL INSULATION OF PIPELINES / TOPLINSKA IZOLACIJA CJEVOVODA / 1 set/1 komplet
| Technical specification / Tehničke karakteristike | Insulation of steel refrigerant piping with a layer of elastomeric rubber insulation with vapor barrier. Insulation thickness min. 20mm. DN 100 - 40m DN 80 - 12m DN 65 - 16m DN 40 - 69m DN 20 - 26m / Izolacija čeličnog cjevovoda rashladnog medija sa slojem izolacije od elastomernog kaučuka sa paronepropusnom branom. Debljina izolacije min. 20mm. DN 100 - 40m DN 80 - 12m DN 65 - 16m DN 40 - 69m DN 20 - 26m
5. | PROTECTIVE LINING OF THE PIPELINE / ZAŠTITNA OBLOGA CJEVOVODA / 1set/1komplet
| Technical specification / Tehničke karakteristike | Aluminum sheet for lining the pipe network of the refrigerant, to the entrance of the pipeline to the building. The item includes all the necessary mounting accessories and small consumables. 12m Painting of steel pipes and equipment with primer with prior rust cleaning and degreasing. 45m2 / Aluminijski lim za oblaganje vanjske cijevne mreže rashladnog medija, do ulaza cjevovoda u objekt. U stavku uključen i sav potreban montažni pribor, te sitni potrošni materijal. 12m Ličenje čeličnih cijevi i opreme temeljnom bojom uz prethodno čišćenje hrđe i odmašćivanje. 45m2
6. | Installation and Commissioning/ Montaža i puštanje u rad / 1 lump sum/ 1 paušal
All the equipments shall be provided, installed, put into operation and tested completely to ensure that the unit is capable of operating to the required technical and quality specifications. All pipe welding material, gas, oxygen, welding wire and other material included. Small consumables material included (screws, nuts, flanges, etc.) Complete suspension accessories for pipe mounting included. The use of a lifting platform, crane or scaffolding for pipeline installation is included. / Sva oprema biti će isporučena, instalirana, puštena u rad i kompletno isprobana da bi se osiguralo da funkcioniranje u potpunosti zadovoljava sve tehničke specifikacije i zahtjeve kvalitete. Uklučen sav materijal za zavarivanje cijevi, plin, kisik, žica za varenje i ostali materijal. Uključeni sitni potrošni materijal (vijci, matice, prirubnice itd.) Uključeni kompletni ovjesni pribor za montažu cijevi. Uključena uporaba podizne platforme, dizalice ili skele za montažu cjevovoda.
Warranty minimum 12 months after final acceptance and commisioning / Garancija minimalno 12 mjeseca nakon završne i puštanja u pogon
7. | Documentation/ Dokumentacija / 1pcs/1kom
| Documentation / Dokumentacija | After the final Acceptance Test, all documentation will be delieverd in electronic (CD-Rom (DVD) and written form with documents in PDF or Excel or dwg format), and will be created in Croatian or English, and includes: / Nakon završetka i prihvaćanja rezultata testne proizvodnje, sva dokumentacija (CD (DVD) s dokumentima u PDF ili Excel ili dwg formatu) bit će izrađena na hrvatskom ili engleskom jeziku, i obuhvaća:
Operating Manual (information about the entire system: system description, maintenance instructions, parts lists, etc.) / Radne upute (informacije o cijelom sustavu: opis sustava, uputama za održavanje, liste dijelovi, itd.)
Drawings (Layout drawings and functionality drawings) / Nacrti (Nacrti postrojenja i funkcionalna shema postrojenja)
8. | Training included / Uključena obuka / 1 lump sum/ 1 paušal
| Training/Obuka | Training included [to be done during the days planned for commissioning and functional testing]. / Obuka uključena [bit će obavljena tijekom perioda planiranog za puštanje sustava u pogon i funkcionalnog ispitivanja].