## Recapitulation
BILL OF QUANTITIES AND TECHNICAL SPECIFICATION
SUBJECT OF PROCUREMENT: PROCUREMENT AND INSTALLATION OF PHOTOVOLTAIC POWER PLANT AND INDOOR AND OUTDOOR LIGHTING
PROCUREMENT NUMBER: 01-22
Unless otherwise defined, the requirements defined in these Technical Specifications represent the minimum technical characteristics that the offered goods, services or works must meet All technical specifications that refer to a product of a particular manufacturer are assumed to refer to that product or equivalent product. The bidder is required to enter the manufacturer, type and model for the key equipment items (marked in gray cells in columns H and I of the workbook sheets). The bidder may enter the manufacturer, type and model for other equipment items if applicable. The bidder is obliged to indicate whether the product contains the required minimum characteristics and enter the offered values ​​for each required characteristic. "
INSTRUCTIONS FOR COMPLETION: fill in the gray marked fields and enter the currency of the offer (HRK or EUR)
BILL OF QUANTITIES RECAPITULATION
| No | DESCRIPTION ITEM | TOTAL PRICE
without VAT
| I | II | III
| 1. | Installation of RES roof photovoltaic power plant system (Map P2/6) | 0
| 2. | Replacing outdoor lighting with more energy efficient ones (Map P3/6) | 0
| 3. | Replacing indoor lighting with more energy efficient ones (Map P4/6) | 0
| Total (without VAT) |  | 0
| VAT |  | 0
| TOTAL (withVAT) |  | 0
Currency of the offer (HRK ili EUR)
Note: It is necessary to indicate the currency of the offer (HRK or EUR) in which the bill of quantities is filled

## 1 PV plant
BILL OF QUANTITIES OF ELECTRICAL INSTALLATIONS More d.o.o. | [5 empty] | Manufacturer, model / type of product | Offered technical specification
Installation of RES roof photovoltaic power plant system (Map P2/6)
No. | Name | Quantity | Unit | Unit price | Price
1. KROVNA FOTONAPONSKA ELEKTRANA
1 | Photovoltaic module with the following characteristics: - technology: Monocrystalline silicon - module power: min 445 Wp - module efficenency (STC): 20,4% or better - allowable system voltage: 1500V | 2586 | piece |  | 0
2 | Photovoltaic converter with the following characteristics: - maximum DC power: 26 A per MPP input - maximum DC voltage: 1100 V - MPPT voltage: 200-1000 V - maximum input current: 40 A - number of groups (loops) per entrance: 2 • Output characteristics: - maximum AC power: 110,00 kVA - nominal AC voltage: 230 (400) V, 50Hz - maximum output current: 168,8 A - maximum efficiency: 98,6% - standard European efficiency: 98,4% •General Information: - inverter topology: inverter without transformer | 9 | piece |  | 0
3 | Communicator for remote monitoring and controlled operation of power plants with RS 485 port, Ethernet port and wireless network | 1 | piece |  | 0
4 | Two-way meter for semi-direct metering of produced electricity, two-way, semi-direct, with saturn measuring transformers 1500/5 A and the corresponding metering terminal box, to be installed in the cabinet GRO_SE | 1 | piece |  | 0
5 | Cabinet GRO_SE dimensions 2000x1600x400 with the following equipment: four-pole switch for separating rated current 1600A (main switch of the power plant) with remote shut-off coil, auxiliary contacts for position signaling and protection activation (and all other functions required in the power approval), 9 compact four-pole power switch with nominal current of 200A, busbar system dimensions 100x10 mm and all other small and connecting accessories required for the operation of the cabinet GRO_SE, IP65 protection, metal cabinet | 1 | piece |  | 0
6 | Solar installation DC cable, tinned, fine wire, UV stabilized, cross section 6mm2 | 9000 | m |  | 0
7 | Alternating cable distribution | 200 | m |  | 0
Cabel XP00-A 4x95mm2
low voltage cable intended for laying in the ground, concrete or cable ducts
8 | Alternating cable distribution | 150 | m |  | 0
-Type P/F 1x25mm2
low voltage cable intended for laying in the ground, concrete or cable ducts
9 | Alternating cable distribution connection from SE GRO to LV distribution in TS | 200 | m |  | 0
-Type H07V-K 240mm2
low voltage cable intended for laying in the ground, concrete or cable ducts
10 | Communication cable | 50 | m |  | 0
-Type S/FTP cat.6
-Ethernet cat6 with protection
11 | PK channel | 150 | m |  | 0
-PK100/60 with lid
12 | PK channel | 100 | m |  | 0
-PK200/60 with lid
13 | PK channel | 50 | m |  | 0
-PK500/160 with lid
14 | MC4 connector set 4 mm2 | 200 | set |  | 0
-male or female set of metal connectors, seals and housings, for connecting rows of photovoltaic modules
15 | Lightning protection installation | 1 | set |  | 0
-stick rods with theonic base height 3m - 10pcs
-Fi 8 aluminum guide for connection to the existing lightning installation - 200m
-connecting accessories
16 | Construction for mounting 2586 photovoltaic panels measuring 2102 x 995 mm on a sloping tin roof, modules in vertical orientation and following the slope of the roof | 1 | set |  | 0
17 | Polyethylene HDPE pipes fi 160mm | 60 | m |  | 0
18 | Supply and installation of solar power plant | 1 | set |  | 0
-delivery of complete power plant equipment to the location
-installing the aluminum construction of the module
-mounting and wiring of modules
-supply and installation of perforated cable ducts and implementation of cable routes
-installing DC cable
- Construction of two concrete manholes with covers for the connection of photovoltaic panels and converters
-assembly and connection of converters
- additional works and installation on the lightning protection installation
-converter configuration according to Croatian grid rules
-configuration of the communicator on the web portal
-connecting and laying AC cables
19 | Voltage-free testing of the solar power plant | 1 | set |  | 0
-insulation testing
- grounding resistance test
-testing protection against contact
-other tests as needed
20 | Commissioning of the solar power plant | 1 | set |  | 0
-development and harmonization with distribution system operator (HEP ODS) of the plan and program of testing the solar power plant
-according to the agreed testing program of the power plant in trial operation with HEP-ODS
- obtaining a Connection Agreement with HEP ODS
- obtaining a contract for the purchase of electricity. energy
- obtaining a contract on the use of the power grid
-development of the Study of the impact of the power plant on the network and the Study of protection settings
-participation in the trial operation of the solar power plant
-testing the protective functions of the power plant according to the agreed plan and program of testing the solar power plant in parallel operation with the network between the contractor and HEP ODS
-preparation of a report on the trial operation of the solar power plant
21 | Measuring electricity quality | 1 | set |  | 0
-according to EN 50160
-according to the conditions from the electricity consent
1. ROOF PHOTOVOLTIAIC POWER PLANT TOTAL: |  |  |  | 0
RACAPITULATION
1. ROOF PHOTOVOLTAIC POWER PLANT
TOTAL |  |  |  |  | 0
VAT |  |  |  |  | 0
TOTAL WITH VAT |  |  |  |  | 0

## 2 Outdoor lighting
BILL OF QUANTITIES OF ELECTRICAL INSTALLATIONS More d.o.o. | [5 empty] | Manufacturer, model / type of product | Offered technical specification
Replacing outdoor lighting with more energy efficient ones (Map P3/6)
Unit price
No | DESCRIPTION ITEM | Unit | Quantity | Unit price | Total
1. CABLE ROUTES AND POWER CABLES
1 | Supply and installation of junction box IP 55 dimensions 100x100mm | piece | 70 |  | 0
2 | Rental and transport - crane for work at height | day | 5 |  | 0
3 | Small connecting material (VAGO couplings 5x2,5) | piece | 500 |  | 0
4 | Small consumables | set | 1 |  | 0
|  |  |  | 1. CABLE ROUTES AND POWER CABLES TOTAL: | 0
No | DESCRIPTION ITEM | Unit | Quantity | Unit price | Total
2. TESTS
1 | "Tests, measurements, and handover of works must be performed in accordance with: in accordance with the Technical Regulations for Low Voltage Electrical Installations (Law gazette No. 5/10), as well as the preparation of the necessary documentation for technical inspection in accordance with the Regulation relating to technical inspection of building (Law gazette No. 108/04): Technical regulations for low-voltage electrical installations (Official Journal 5/10) - Technical regulations for lightning protection systems on buildings (OJ 87/08, 33/10) The complete documentation must be bound in the "MINUTES BOOK" with the appropriate content, which must contain individual MINUTES (atests) with the test results, as follows: - cable insulation test, - testing the continuity of the protective conductor and the connection of metal masses to the equipotential bonding. - testing the operation of protective measures - protection against increased contact voltage, settings of protective devices, control of mechanical protection and required IP protection, adjustment of control and signal circuits - preparation and submission of test lists for performed controls, settings and tests, - submission of the Certificate of Conformity of the Product with the Basic Requirements and other necessary attestation sheets - delivery of guarantee certificates - submission of reports on performed works - technical instructions for operation and maintenance in the Croatian language which must contain a description of the system, technical data, required block diagrams, - description of operation, description of maintenance work, description of test procedures " | piece | 1 |  | 0
|  |  |  | 2. TESTS: | 0
3. LIGHTING INSTALATION
Installation and connection of lamps, complete with light bulbs:
OUTDOOR LIGHTS
22.OUTDOOR LIGHTING | Disassembly and disposal in accordance with the regulations for the disposal of waste electrical and electronic equipment - WTFe and metal halide reflectors 250W, 400W and 2000W (H = 5-10m) | piece | 60 |  | 0
- | Supply of lamps; complete with LED light sources, max 83W; min. 9000Lm; pole mounting bracket | piece | 27 |  | 0
- | Reflector supply; complete with LED light sources, max 100W; min. 13000Lm | piece | 9 |  | 0
- | Reflector supply; complete with LED light sources, max 150W; min. 20400Lm | piece | 13 |  | 0
- | Supply of lamps; complete with LED light sources, max 56W; min. 6100Lm; pole mounting bracket | piece | 11 |  | 0
- | Supply and installation of adapters for mounting the lamp on a pole or roof console | piece | 60 |  | 0
- | Installation and connection of the lamp (H = 5-10m) | piece | 60 |  | 0
- | Supply and installation of circuit breaker B 6A | piece | 60 |  | 0
|  |  |  | 3. LIGHTING INSTALATION TOTAL: | 0
REKAPITULACIJA
| 1. CABLE ROUTES AND POWER CABLES |  |  |  | 0
| 2. TESTS |  |  |  | 0
| 3. LIGHTING INSTALLATION |  |  |  | 0
| TOTAL |  |  |  | 0
| VAT |  |  |  | 0
| TOTAL WITH VAT |  |  |  | 0

## 3 Indoor lighting
BILL OF QUANTITIES OF ELECTRICAL INSTALLATIONS More d.o.o. | [5 empty] | Manufacturer, model / type of product | Offered technical specification
Replacing indoor lighting with more energy efficient ones (Map P4/6)
No | DESCRIPTION ITEM | Unit | Quantity | Unit price | Total
1. CABLE ROUTES AND POWER CABLES
1 | Supply and installation of junction box IP 55 dimensions 100x100mm | piece | 114 |  | 0
2 | Rental and transport - crane for work at height | day | 15 |  | 0
3 | Small connecting material (WAGO couplings 5x2,5) | piece | 2500 |  | 0
4 | Small consumables | set | 1 |  | 0
5 | Supply and installation of metal channels dimesnions 100x20 mm | m | 200 |  | 0
6 | Supply and installation of B16A circuit breakers | piece | 20 |  | 0
7 | Supply and installation 0-1 two-pole cam switch | piece | 20 |  | 0
| 1. CABLE ROUTES AND POWER CABLES TOTAL: |  |  |  | 0
No | DESCRIPTION ITEM | Unit | Quantity | Unit price | Total
2. TESTS
1 | "Tests, measurements, and handover of works must be performed in accordance with: in accordance with the Technical Regulations for Low Voltage Electrical Installations (Law gazette No. 5/10), as well as the preparation of the necessary documentation for technical inspection in accordance with the Regulation relating to technical inspection of building (Law gazette No. 108/04): Technical regulations for low-voltage electrical installations (Official Journal 5/10) - Technical regulations for lightning protection systems on buildings (OJ 87/08, 33/10) The complete documentation must be bound in the "MINUTES BOOK" with the appropriate content, which must contain individual MINUTES (atests) with the test results, as follows: - cable insulation test, - testing the continuity of the protective conductor and the connection of metal masses to the equipotential bonding. - testing the operation of protective measures - protection against increased contact voltage, settings of protective devices, control of mechanical protection and required IP protection, adjustment of control and signal circuits - preparation and submission of test lists for performed controls, settings and tests, - submission of the Certificate of Conformity of the Product with the Basic Requirements and other necessary attestation sheets - delivery of guarantee certificates - submission of reports on performed works - technical instructions for operation and maintenance in the Croatian language which must contain a description of the system, technical data, required block diagrams, - description of operation, description of maintenance work, description of test procedures " | piece | 1 |  | 0
| 2. TESTS |  |  |  | 0
No | DESCRIPTION ITEM | Unit | Quantity | Unit price | Total
3. LIGHTING INSTALATION
Installation and connection of lamps, complete with light bulbs:
MORE d.o.o.
WAREHOUSE | Disassembly and disposal in accordance with the regulations for the disposal of waste electrical and electronic equipment - Broadband reflector 400W ( H=6,00m ) | piece | 12 |  | 0
- | Supply of industrial lamp; set with LED light sources max.150W, min. 19000 Lm | piece | 20 |  | 0
- | Installation and connection of industrial lamps (h = 6,00m) | piece | 20 |  | 0
- | Cable NYY-J 3x2.5 mm2. The unit price includes delivery, installation, preparation of the cable route and connection of cables at both ends. | m | 150 |  | 0
- | Supply and installation of PNT pipes fi 25 | m | 150 |  | 0
PRESSING AND ASSEMBLING OF PANELS | Disassembly and disposal in accordance with the regulations for the disposal of waste electrical and electronic equipment - Broadband reflectorr 400W ( H=6,00m ) | piece | 9 |  | 0
| - conductor ( H=6,00m ) | m | 100 |  | 0
- | Supply of industrial lamp; set with LED light sources max.150W, min. 19000 Lm | piece | 12 |  | 0
- | Installation and connection of industrial lamps (h = 6,00m) | piece | 12 |  | 0
- | Cable NYY-J 3x2.5 mm2. The unit price includes delivery, installation, preparation of the cable route and connection of cables at both ends. | m | 200 |  | 0
- | Supply and installation of PNT pipes fi 25 | m | 200 |  | 0
CUTTING AND DIMENSING | Disassembly and disposal in accordance with the regulations for the disposal of waste electrical and electronic equipment - Broadband reflector 400W ( H=6,00m ) | piece | 42 |  | 0
| - conductor ( H=6,00m ) | m | 300 |  | 0
- | Supply of industrial lamp; set with LED light sources max.150W, min. 19000 Lm | piece | 32 |  | 0
- | Supply of industrial lamps; complete with LED light sources max.200W, min. 26000 Lm | piece | 20 |  | 0
- | Installation and connection of industrial lamps (h = 6,00m) | piece | 52 |  | 0
- | Cable NYY-J 3x2.5 mm2. The unit price includes delivery, installation, preparation of the cable route and connection of cables at both ends. | m | 600 |  | 0
- | Supply and installation of PNT pipes fi 25 | m | 400 |  | 0
SAWMILL | Disassembly and disposal in accordance with the regulations for the disposal of waste electrical and electronic equipment - Broadband reflector 400W i fluo 2x58W ( H=6,00m ) | piece | 21 |  | 0
| - conductor ( H=6,00m ) | m | 150 |  | 0
- | Supply of industrial lamp; set with LED light sources max.150W, min. 19000 Lm | piece | 30 |  | 0
- | Installation and connection of industrial lamps (h = 6,00m) | piece | 30 |  | 0
- | Cable NYY-J 3x2.5 mm2. The unit price includes delivery, installation, preparation of the cable route and connection of cables at both ends. | m | 500 |  | 0
- | Supply and installation of PNT pipes fi 25 | m | 400 |  | 0
3. LIGHTING INSTALATION TOTAL: |  |  |  |  | 0
RECAPITULATION
| 1. CABLE ROUTES AND POWER CABLES |  |  |  | 0
| 2. TESTS |  |  |  | 0
| 3. LIGHTING INSTALATION |  |  |  | 0
| TOTAL (HRK) |  |  |  | 0
| VAT |  |  |  | 0
| OVERALL (HRK) |  |  |  | 0