## Sheet1
Uputa o načinu popunjavanja: • Ponuditelj je obvezan ispuniti Troškovnik po svim traženim stavkama, na način da popuni stupac "Ponuđene specifikacije" prema opisima u stupcu "Tražene specifikacije" te da upiše proizvođača i model u za to predviđeno mjesto ako je primijenjivo te da popuni polje "Ponuđena dostupnost certifikata". Ponuđena roba mora u cijelosti zadovoljiti minimalne karakteristike koje su opisane u tehničkoj specifikaciji ili biti bolja od opisanih specifikacija. • Ponuditelj ne smije mijenjati navedene tražene tehničke specifikacije • Za sve stavke Troškovnika u kojima se uz navedene tehničke specifikacije traži norma, oznaka ili pak marka, patent, tip ili određeno podrijetlo, ponuditelj može ponuditi „ili jednakovrijedno“. • U stupac "Jedinična cijena bez PDV-a ponuditelj upisuje jedinične cijene u dvije decimale. Ponuditelj upisuje valutu ponude u za to predviđenu ćeliju.
Instructions on filling out the form: • The Bidder is obliged to fill in the Cost Sheet for all required items, by entering the column "Offered specifications" according to descritions from the column "Requested specifications" and by entering the producer and model name if applicable and by entering "Offered available certificate". The offered goods must fully meet the minimum characteristics described in the technical specification or be better than the described specifications. • The bidder may not change the stated required technical specifications • For all items of the Cost Sheet in which, in addition to the stated technical specifications, a standard, marking or trademark, patent, type or certain origin is required, the bidder may bid "or equivalent". • In the column "Unit price excluding VAT", the bidder enters unit prices rounded to two decimal places.The bidder enters the bid currency in the cell provided.
Rashladno postrojenje Chiller plant
Redni broj / No. | Tražene specifikacije / Requested specifications | Ponuđene specifikacije / Offered specifications
1 | Cirukulacijske pumpe Circulation pumps
Pumpni sistem voda/glikol 1 Water/glycol pumping system 1
Naziv proizvođača i modela / Producer and model name
Pumpni sustav koji se sastoji od centrifugalnih inline pumpi, s VFD pogonima i PID regulatorima s kontrolom diferencijalnog tlaka Pumping system consisting centrifugal in- line pumps , with VFD drives and PID regulators with differential pressure control
Sustav pumpanja konfiguriran kao dvostruki (1 radna pumpa + 1 stand by pumpa) na skid platformi sa pripadajučim ventilima ,filterima ,vibracijskim spojevima , temp senzorima , senzorima tlaka i na izlazu protokomjer (senzor protoka) The pumping system is configured as double (1 working pump + 1 stand by pump) on the skid platform with associated valves, filters, vibration joints, temp sensors, pressure sensors and a flow meter (flow sensor) at the output
Opća specifikacija: - Ukupni zahtjev za protokom: po svakoj pumpi minimalno 240 m3/h - Sustav promjenjive brzine s VFD-om - Ukupni pad tlaka: minimalno 70 m - Tekući medij: smjesa glikol/voda za temperature do -40°C - Kućište pumpe; lijevano željezo/ss čelik ili jednakovrijedan - Priključak pumpi: prirubnički - Pumpe s namjenski ugrađenim VFD i PID regulatorom ili sličnim - Napajanje 400 V / 50 Hz General specification: - Total flow requirement: for each pump minimum 240 m3/h - Variable speed system with VFD - Total pressure drop: minimum 70 m - Fluid media: glycol /water mixture for temeperatures up to -40°C - Pump housing; cast iron/ss steel or equivalent - Pumps connection:flanged - Pumps with dedicated built -on VFD and PID regulator or simillar - Powersupply 400 V / 50 Hz
Opseg isporuke: - Kompletan pumpni sustav sastavljen i ožičen - Tehnička dokumentacija rukovanja i održavnja - Certifikati/atesti opreme Scope of delivery: - Complete pumping system assembled and prewired - Technical documentation of operation and maintenance of all devices and equipment - Equipment cerificates
Pumpni sistem voda/glikol 2 Water/glycol pumping system 2
Naziv proizvođača i modela / Producer and model name
Pumpni sustav koji se sastoji od centrifugalnih inline pumpi, s VFD pogonima i PID regulatorima s kontrolom diferencijalnog tlaka Pumping system consisting of centrifugal inline pumps, with VFD drives and PID regulators with differential pressure control
Sustav pumpanja konfiguriran kao dvostruki( 1 radna pumpa + 1 stand by pumpa) na skid platformi sa pripadajučim ventilima ,filterima ,vibracijskim spojevima , temp senzorima , senzorima tlaka i na izlazu protokomjer ( senzor protoka) The pumping system is configured as double (1 working pump + 1 stand by pump) on the skid platform with associated valves, filters, vibration joints, temp sensors, pressure sensors and a flow meter (flow sensor) at the output.
Pumpni sustav ugrađađen na platformi( pomorskom objektu) Pumping system installed on the platform (marine object)
Opća specifikacija: - Ukupni zahtjev za protokom: minimalno 30 m3/h - Sustav promjenjive brzine s VFD-om - Ukupni pad tlaka: minimalno 50 m - Tekući medij: smjesa glikol/voda za temperature do -40°C - Kućište pumpe: lijevano željezo/ss čelik ili jednakovrijedno - Ugradnja na pomorski objekt - Priključak pumpi: prirubnički - Pumpe s namjenski ugrađenim VFD i PID regulatorom ili sličnim - Napajanje 400 V / 50 Hz General specification: - Total flow requirement: minimum 30 m3/h - Variable speed system with VFD - Total pressure drop: minimum 50 m - Liquid medium: glycol/water mixture for temperatures up to -40°C - Pump housing; cast iron/ss steel or equivalent - Installation on a marine facility - Pumps connection: flanged - Pumps with dedicated built -on VFD and PID regulator or simillar - Power supply 400 V / 50 Hz
Opseg isporuke: - Kompletan pumpni sustav sastavljen i ožičen - Tehnička dokumentacija rukovanja i održavnja - Certifikati/atesti opreme Scope of delivery: - Complete pump system assembled and wired - Technical documentation of operation and maintenance of all devices and equipment - Equipment certificates/atests
Redni broj / No. | Opis stavke / Item description | Jedinica mjere / Unit | Količina / Quantity | Jedinična cijena bez PDV-a / unit price excluding VAT | Ukupno / Total price excluding VAT
1 | Cirukulacijske pumpe (Pumpni sistem voda/glikol 1 + Pumpni sistem voda/glikol 2) Circulation pumps (Water/glycol pumping system 1 + Water/glycol pumping system 2) | kompl/set | 1 |  | 0
T | Cijena transporta DDP Brodosplit, PDV neplaćen Transport price DDP Brodosplit, VAT excluded | kompl/set | 1 |  | 0
| Rok isporuke: maksimalno 4 mjeseca od uplate avansa Delivery deadline: maximum 4 months since advance payment |  |  | SVEUKUPNO BEZ PDV-a / TOTAL SUM excluding VAT | 0
| Plaćanje: 50% avansa ukupnog iznosa, 50% nakon testiranja, a prije isporuke Payment: 50% advance of the total amount, 50% after testing and before delivery |  |  | IZNOS PDV-a / VAT ammount
|  |  |  | SVEUKUPNO S PDV-om / TOTAL SUM including VAT | 0
VALUTA PONUDE / BID CURRENCY EUR ili USD / EUR or USD