PRILOG 2 POZIVA NA DOSTAVU PONUDA

TROŠKOVNIK /

ANNEX 2 OF INVITATION TO TENDER

BILL OF QUANTITIES

Ev. broj nabave: / Procurement number: 03-2021-SCN

Predmet nabave: / Subject of procurement: Baterijski spremnik električne energije (BSEE) / Battery Energy Storage System (BESS)

| Predmet br. / Item | Predmet nabave / Subject of procurement | Nudi se / Is offered | Jedinica mjere / Unit | Količina / Quantity | Jedinična cijena u EUR (bez PDV-a)* / Unit price in EUR net of VAT* | Ukupna cijena u EUR (bez PDV-a)*/ Total price in EUR net of VAT* |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 |
| 1. | Baterijski spremnik električne energije (BSEE) / Battery Energy Storage System (BESS) BSEE Tehnička specifikacija: BSEE energetski kapacitet 490- 575 kWh, kod DoD > 90% BESS nominalni napon: 500-700V DC Konfiguracija: modularna, baterijski blokovi s mogućnosti paralelnog spajanja blokova Hlađenje: mješavina vode i etilen glikola 50% Nominalna snaga punjenja/pražnjenja: 490-550 kW Kemija baterija: LiPO4 (LFP) Stupanj učinkovitosti: min 90 % Očekivani broj ciklusa: min 5500 uz uvjete; DoD= 90%, SoH= 70%, radna temperatura 18 oC Temperaturno područje rada (vodeno hlađenje): min. -20 oC do + 50 oC Smještajna konfiguracija: standardni kontejner (20 ili 40 stopa) Pomoćni sustavi nužni za rad baterijskog spremnika: - Upravljački sustav - DC and AC sabirnički i kabelski razvod - Rashladni sustav - Sustav klimatizacije (HVAC) i zašite od požara (FPS)/ BESS Technical specification BESS energy capacity: 490 - 575 kWh at DoD > 90% BESS nominal voltage: 500-700V DC Layout: modular configuration; battery banks; parallel connection ability Cooling: water - ethylen glycol mixture 50% Nominal charge/discharge power: 490-550kW Battery cell technology:LiPO4 (LFP) Efficiency: min 90 % Expected number of cycles: min 5500 under conditions; DoD= 90%, SoH= 70%, at working temperature 18 oC Environment operating temperature (liquid cooling): min. -20 oC do + 50 oC Layout design: standard container (20 or 40 feet) Auxiliary mandatory subsystems: - Control system - DC and AC distribution and cabling - Cooling system - HVAC and fire protection system (FPS) |  | kom / piece | 1 |  |  |
|  | Cijena ponude u EUR bez poreza na dodanu vrijednost*: / Total price in EUR net of VAT: |  |  |  |  |  |

U / In                               ,                    2023 . g.

ZA PONUDITELJA / ON BEHALF OF THE TENDERER:

________________________________________________.

(ime, prezime i potpis ovlaštene osobe) /

(Name, surname and signature of the authorised representative)