## Sheet1
Uputa o načinu popunjavanja: • Ponuditelj je obvezan ispuniti Troškovnik po svim traženim stavkama, na način da popuni stupac "Ponuđene specifikacije" prema opisima u stupcu "Tražene specifikacije" te da upiše proizvođača i model u za to predviđeno mjesto ako je primijenjivo te da popuni polje "Ponuđena dostupnost certifikata". Ponuđena roba mora u cijelosti zadovoljiti minimalne karakteristike koje su opisane u tehničkoj specifikaciji ili biti bolja od opisanih specifikacija. • Ponuditelj ne smije mijenjati navedene tražene tehničke specifikacije • Za sve stavke Troškovnika u kojima se uz navedene tehničke specifikacije traži norma, oznaka ili pak marka, patent, tip ili određeno podrijetlo, ponuditelj može ponuditi „ili jednakovrijedno“. • U stupac "Jedinična cijena bez PDV-a ponuditelj upisuje jedinične cijene u dvije decimale. Ponuditelj upisuje valutu ponude u za to predviđenu ćeliju.
Instructions on filling out the form: • The Bidder is obliged to fill in the Cost Sheet for all required items, by entering the column "Offered specifications" according to descritions from the column "Requested specifications" and by entering the producer and model name if applicable and by entering "Offered available certificate". The offered goods must fully meet the minimum characteristics described in the technical specification or be better than the described specifications. • The bidder may not change the stated required technical specifications • For all items of the Cost Sheet in which, in addition to the stated technical specifications, a standard, marking or trademark, patent, type or certain origin is required, the bidder may bid "or equivalent". • In the column "Unit price excluding VAT", the bidder enters unit prices rounded to two decimal places.The bidder enters the bid currency in the cell provided.
Geomembrana / folija za hidroizolaciju sa alatom za montažu Geomembrane / foil for waterproofing with assembly tool
Redni broj / No. | Tražene specifikacije / Requested specifications | Ponuđene specifikacije / Offered specifications
1 | GeoMembrana /folija za hidroizolaciju spremnika Geomembrane / foil for tank hydroisolation
Geomembrana /folija za hidroizolaciju spremnika vode za dugotrajni smještaj tekućine prema EN 13 361 ili jednakovrijedan Osnovne karakteristike : materijal folije : HDPE ( Polyethilen visoke gustoće) debljina folije : 1 mm (minimalna vrijednost) Gustoća materijala:folije : minimalno 920 kg/m3 vlačna čvrstoća (kN/m ) : minim 10 kN/m Prekidna Vlačna čvrstoća (kN/m ) minimalno 25 kN/m Otpornost na trganje : minimalno 110 N Otpornost na toškasto probijanje .minnimalno 300 N Vodotijesnost prema EN 14150 ili jednakovrijedan Dugotrajno spremanje tekučine i leda Geomembrane/foil for tank hydroisolation for longterm liquid containment according to EN 13 361 or equivalent Basic characteristics: Mebrane /foil material HDPE (high-density polyethylene) Foil thickness: 1 mm (minimum value) Material density: film: minimum 920 kg/m3 Tensile strength (kN/m) minimum 10 kN/m Breaking Tensile strength (kN/m) minimum 25 kN/m Tear resistance: minimum 110 N Point puncture resistance: minimum 300 N Water tightness according to EN 14150 or equivalent Long-term storage of liquid and ice
Dugotrajna stabilinost i održavanje mehaničkih svojstava na temperaturama ispod minimalno -20C Isporuka u roli :minimalne dužine 69 metara i minimalne širine 5,70 metara Long-term stability and maintenance of mechanical properties at temperatures below at least -20C Delivery in rolls width minimun length of 69 metres and with minimum width of 5,70 metres
2 | Alat za montažu geomebrane Geomembrane installation tool
Poluautomatski aparat za zavaivanje spojeva HDPE mebrane Osnovne karakteristike : minimalno 700 W snage Za temeperature grijanja :minimalno od 0-400C ( regulirano Zavarivanje spojeva HDPE mebrane do debljina 1 mm Brzine zavarivanja : minimalno 0,5 -4 m/min Napajanje : 230 V / 50 Hz Klassa električne zaštite uređaja : KLAsa II Semi-automatic device for welding joints of HDPE membranes Basic characteristics: minimum 700 W power For heating temperatures: minimum from 0-400C (regulated) Welding joints of HDPE membranes up to a thickness of 1mm Welding speeds: minimum 0.5-4 m/min Power supply: 230 V / 50 Hz Electrical protection class of the device: CLASS II
Opseg isporuke: Geomebrana prema specifikacijama Tvornica mora biti u skladu sa sustavom kvalitete ISO 9001 ili jednakovrijedan Izjava o svojstvima (DOP) ili izjava sukladnosti za geomebranu Upute rukovanja za uređaje Scope of delivery: Geomembrane according to specifications Factory must comply with ISO 9001 quality system) or equivalent Declaration of properties (DOP) or declaration of conformity for geomembrane Operating instructions for device
Redni broj / No. | Opis stavke / Item description | Jedinica mjere / Unit | Količina / Quantity | Jedinična cijena bez PDV-a / unit price excluding VAT | Ukupno / Total price excluding VAT
1 | GeoMembrana /folija za hidroizolaciju spremnika Geomembrane / foil for tank hydroisolation | m2/m2 | 10994 |  | 0
2 | Alat za montažu geomebrane Geomembrane installation tool | kompl/set | 2 |  | 0
| EXW paritet EXW parity |  |  | SVEUKUPNO BEZ PDV-a / TOTAL SUM excluding VAT | 0
| Plaćanje: 50% avansi 50 % prije isporuke Payment: 50 % advance and 50% before delivery |  |  | IZNOS PDV-a / VAT ammount
| Rok isporuke: najkasnije do 20.12.2023. Delivery deadline: maximum up to 20 th of December 2023. |  |  | SVEUKUPNO S PDV-om / TOTAL SUM including VAT | 0
VALUTA PONUDE / BID CURRENCY EUR ili USD / EUR or USD